{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["监督检验报告信息","Sheet1"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"监督检验报告信息","index":0,"n_rows":10,"n_cols":14,"rows_kept":10,"merged":[[0,0,0,11],[1,0,1,13],[2,0,2,13],[3,0,3,13]],"flags":["formulas_cached_only"]}
["2024年手提式灭火器产品质量市监督抽查结果"]
["本次通过网络平台抽查了5家单位的5批次产品。\n监督抽查不合格产品检出率为40%。\n依据 GB 4351.1-2005 《手提式灭火器 第1部分：性能和结构要求》等标准，对质量，20℃温度喷射性能试验，水压试验（筒体），爆破试验，灭火剂和驱动气体（干粉灭火剂）-第一主要组分含量等5个项目进行了检验。\n抽查发现有2家企业的2批次产品不符合相关标准要求，不合格项目为：质量，灭火剂和驱动气体（干粉灭火剂）-第一主要组分含量。我局已依法对不合格产品开始了后处理工作。\n具体抽查结果见附件。\n"]
["附件"]
["2024年手提式灭火器产品质量市级监督抽查结果汇总表"]
["序号","抽样领域","产品名称","受检单位名称","统一社会信用代码","标称生产者名称","生产日期或批号","规格型号","商标","抽查结果","不合格项目","抽样日期","行政区划","承检单位"]
[1,"电商领域","手提式干粉灭火器","李沧区蓝岛便利店","92370213MA3P0H650R","江苏恒佑消防器材有限公司","2024-03/—","MFZ/ABC4型","/","不合格","灭火剂和驱动气体（干粉灭火剂）-第一主要组分含量","2024-05-07","李沧区","青岛市产品质量检验研究院"]
[2,"电商领域","手提式干粉灭火器","青岛福满阳贸易有限公司","91370213MACB7MUE2F","山东亿嘉消防器材有限公司","2023-07/—","MFZ/ABC2","/","不合格","质量、灭火剂和驱动气体（干粉灭火剂）-第一主要组分含量","2024-05-06","李沧区","青岛市产品质量检验研究院"]
[3,"电商领域","手提式干粉灭火器","青岛乐岛便利店有限公司","91370203MA3QC9CK66","徐州竫宇消防器材有限公司","2024-04/—","MFZ/ABC4","/","所检项目符合标准","/","2024-05-10","市北区","青岛市产品质量检验研究院"]
[4,"电商领域","手提式干粉灭火器","青岛精优创品商贸有限公司","91370213MACLADT10T","江苏恒佑消防器材有限公司","2024-03/—","MFZ/ABC2型","/","所检项目符合标准","/","2024-05-08","李沧区","青岛市产品质量检验研究院"]
[5,"电商领域","手提式干粉灭火器","北京京东叁佰陆拾度电子商务有限公司","9111030266052765XB","青岛楼山消防器材厂有限公司","2024-05/—","MFZ/ABC1型","/","所检项目符合标准","/","2024-05-13","李沧区","青岛市产品质量检验研究院"]

{"sheet":"Sheet1","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}